## Benign Behaviours
Normal operation |  |  | Complex emergency operation (two faults occur simultaneously)
No faults happen |  | Action -- normal | Fault 1 | Fault 2 | Actions combo | Fault 1 | Fault 2 | Actions combo
| 1 physical behaviours | 1 network behaviours | 66Bus1 | 66Bus2 | Protection 1 & 2 | 22Bus1 | 22Bus2 | Protection 3 & 4
|  |  | 66Bus1 | TRSF2 |  |  | 1 | 1
Simple emergency operation (one phase-to-phase fault occurs) |  |  | 66Bus2 | TRSF1 |  | 22Bus1 | FDR1 | Protection 3 & 5
Fault ID | Fault location description | Actions | TRSF1 | TRSF2 |  | 22Bus1 | FDR2 | Protection 3 & 6
66Bus1 | Among CB1_66kV, CB2_66kV, and Transformer1 | Protection 1 | 66Bus1 | TRSF1 | Protection 1 | 22Bus1 | FDR3 | Protection 3 & 7
66Bus2 | Among CB2_66kV, CB3_66kV, and Transformer2 | Protection 2 | 66Bus2 | TRSF2 | Protection 2 | 22Bus1 | FDR4 | Protection 3 & 8
TRSF1 | Between transformer1 and CB_TRSF1 | Protection 1 |  | 6 | 1 | 22Bus2 | FDR1 | Protection 4 & 5
TRSF2 | Between transformer2 and CB_TRSF2 | Protection 2 | 66Bus1 | 22Bus1 | Protection 1 & 3 | 22Bus2 | FDR2 | Protection 4 & 6
22Bus1 | Between CB1_22kV and CB_FDR1 | Protection 3 | TRSF1 | 22Bus1 |  | 22Bus2 | FDR3 | Protection 4 & 7
22Bus2 | Between CB3_22kV and CB_FDR2 | Protection 4 | 66Bus1 | 22Bus2 | Protection 1 & 4 | 22Bus2 | FDR4 | Protection 4 & 8
FDR1 | Between CB_FDR1 and FDR1 load | Protection 5 | TRSF1 | 22Bus2 |  |  | 8 | 8
FDR2 | Between CB_FDR2 and FDR2 load | Protection 6 | 66Bus2 | 22Bus1 | Protection 2 & 3 | FDR1 | FDR2 | Protection 5 & 6
FDR3 | Between CB_FDR3 and FDR3 load | Protection 7 | TRSF2 | 22Bus1 |  | FDR1 | FDR3 | Protection 5 & 7
FDR4 | Between CB_FDR4 and FDR4 load | Protection 8 | 66Bus2 | 22Bus2 | Protection 2 & 4 | FDR1 | FDR4 | Protection 5 & 8
| 10 physical behaviours | 8 network behaviours | TRSF2 | 22Bus2 |  | FDR2 | FDR3 | Protection 6 & 7
|  |  |  | 8 | 4 | FDR2 | FDR4 | Protection 6 & 8
Simple emergency operation (Breaker failure protection) |  |  | 66Bus1 | FDR1 | Protection 1 & 5 | FDR3 | FDR4 | Protection 7 & 8
Fault ID | Fault location description | Actions | TRSF1 | FDR1 |  |  | 6 | 6
22Bus1 | Between CB1_22kV and CB_FDR1 | Protection 3 failed, Protection 9 activates. | 66Bus1 | FDR2 | Protection 1 & 6
22Bus2 | Between CB3_22kV and CB_FDR2 | Protection 4 failed, Protection 10 activates. | TRSF1 | FDR2
FDR1 | Between CB_FDR1 and FDR1 load | Protection 5 failed, Protection 11 activates. | 66Bus1 | FDR3 | Protection 1 & 7 | In totoal | 45 | 28
FDR4 | Between CB_FDR4 and FDR4 load | Protection 8 failed, Protection 12 activates. | TRSF1 | FDR3
| 4 physical behaviours | 4 network behaviours | 66Bus1 | FDR4 | Protection 1 & 8
|  |  | TRSF1 | FDR4
|  |  | 66Bus2 | FDR1 | Protection 2 & 5
|  |  | TRSF2 | FDR1
|  |  | 66Bus2 | FDR2 | Protection 2 & 6
|  |  | TRSF2 | FDR2
|  |  | 66Bus2 | FDR3 | Protection 2 & 7
|  |  | TRSF2 | FDR3
|  |  | 66Bus2 | FDR4 | Protection 2 & 8
|  |  | TRSF2 | FDR4
|  |  |  | 16 | 8

## Normal Action
Normal | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | close | close | close | close | close
IED_BFP | [15 empty] | close | close | close | close | close

## Protection Actions
Simple protection 1 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | open | open | open | close
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | close | close | close | close | close
IED_BFP | [15 empty] | close | close | close | close | close
Simple protection 2 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | open | open | close
IED_FDR | [8 empty] | close | close | close | close | close | close | close
IED_BFP | [15 empty] | close | close | close | close | close
Simple protection 3 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | open | close | close | close | close | close | close
IED_BFP | [15 empty] | close | close | close | close | close
Simple protection 4 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | open | close | close | close | close
IED_BFP | [15 empty] | close | close | close | close | close
Simple protection 5 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | close | open | close | close | close
IED_BFP | [15 empty] | close | close | close | close | close
Simple protection 6 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | close | close | open | close | close
IED_BFP | [15 empty] | close | close | close | close | close
Simple protection 7 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | close | close | close | open | close
IED_BFP | [15 empty] | close | close | close | close | close
Simple protection 8 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | close | close | close | close | open
IED_BFP | [15 empty] | close | close | close | close | close
Simple protection 9 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | open | close | close | close | close | close | close
IED_BFP | [15 empty] | open | close | close | open | close
Simple protection 10 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | open | close | close | close | close
IED_BFP | [15 empty] | close | open | close | open | close
Simple protection 8 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | close | open | close | close | close
IED_BFP | [15 empty] | close | close | open | close | close
Simple protection 8 | Publish GOOSE APPID 0X8001 |  |  |  | Publish GOOSE APPID 0X8002 |  |  |  | Publish GOOSE APPID 0X8003 | [6 empty] | Publish GOOSE APPID 0X8004
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_22kV | CB2_66kV | CB3_66kV | CB_TRSF2 | CB2_22kV | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4 | CB_TRSF1 | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV
IED_TRSF1 | close | open | close | open
IED_TRSF2 |  |  |  |  | open | close | close | open
IED_FDR | [8 empty] | close | close | close | close | close | close | open
IED_BFP | [15 empty] | close | close | close | close | open