## Sheet1
Fault occurs between A & B, monitoring current values exceed thresholds, and Open certain CBs
A | B | Monitoring factors | Threshold | Open CBs | Fault location | Circuit Breaker failure protection condition | Circuit Breaker failure protection actions
CB_FDR1 | RLC load 1 | Fault_on_FDR1_Current | >500 | CB_FDR1 | Feeders | If CB_FDR1 fails to open in 2 seconds | BFP activated, open CB1_22KV
CB_FDR2 | RLC load 2 | Fault_on_FDR2_Current |  | CB_FDR2
CB_FDR3 | RLC load 3 | Fault_on_FDR3_Current |  | CB_FDR3
CB_FDR4 | RLC load 4 | Fault_on_FDR4_Current |  | CB_FDR4 |  | If CB_FDR4 fails to open in 2 seconds | BFP activated, open CB3_22KV
CB_FDR1 | CB_TRSF1 | Fault_on_22BUS1_Current |  | CB1_22KV | 22KV BUS | If CB1_22KV fails to open in 2 seconds | BFP activated, open CB2_22KV and CB_TRSF1
CB_FDR1 | CB1_22KV
CB_FDR4 | CB_TRSF2 | Fault_on_22BUS2_Current |  | CB3_22KV |  | If CB3_22KV fails to open in 2 seconds | BFP activated, open CB2_22KV and CB_TRSF2
CB_FDR4 | CB1_22KV
CB_TRSF1 | Transformer1 | Fault_on_TRSF1_Current |  | CB_TRSF1, CB1_66KV, CB2_66KV | Transformer
Within transformer1
CB_TRSF2 | Transformer2 | Fault_on_TRSF2_Current |  | CB_TRSF2, CB3_66KV, CB2_66KV
Within transformer2
CB1_66KV | CB2_66KV | Fault_on_66BUS1_Current |  | CB_TRSF1, CB1_66KV, CB2_66KV | 66KV BUS
CB1_66KV | Transformer1
CB2_66KV | Transformer1
CB3_66KV | CB2_66KV | Fault_on_66BUS2_Current |  | CB_TRSF2, CB3_66KV, CB2_66KV
CB3_66KV | Transformer2
CB2_66KV | Transformer2